## Schedule B (i)
Returnable Schedule B (i) Central Management System
Tenderers should note that a non-compliant or partially compliant response to a Mandatory Requirement may result in the tender being rejected
|  | Recommendation about whether each item should be Mandatory Requirement (MR) or Scored Response (SR) | Short Response | Further Details | Links
4.2 Physical Features and Requirements
A. The System shall use a Central Management System that is hosted by [Select ONE or more of the following options]:
| 1. The User or a User specified Third Party | MR
| 2. The Vendor. Hosting fees to be incorporated in first cost | MR
| 3. The Vendor. Hosting fees to be separately identified as a recurring cost | MR
| 4. The Vendor. “In Australia” or “In New Zealand”, if data sovereignty is a factor | MR
| 5. Other - Vendor proposed option | MR
| B. The Vendor shall provide a description of the overall architecture, availability, reliability, scalability and security approach of the System irrespective of the hosting location and arrangements. | MR
C. The Vendor shall provide sample screen images depicting the following features and functions:
| 1. Commissioning: Installation and Configuration process of a new Light point Controller | MR
| 2. Inventory: Luminaire/Light Point Controller location with selectability on maps (e.g. using a lasso tool), description with multiple attributes (including identifier, type, model, supplier, address, etc.), ability to colour code assets and obtain a street level view of asset location – e.g. Google Street View. | MR
| 3. Schedules/Calendars: Defining schedules, assigning schedules to days and applying these calendars to groups of Light Point Controllers | MR
| 4. Failure analysis: Display Luminaire and electrical failures on maps for the whole city (very high zoom level) and for a particular geographical section (low zoom level, e.g. a block) on road maps as well as satellite map, from several map providers. | MR
| 5. Real time view: Light Point Controller and Gateway status (i.e. online, online reporting error, offline, failures), luminaire status (On, Off, dimming level) | MR
| 6. Data analytics: System power quality on any particular luminaire (including current requirements, peak requirement in last prescribed time period) and generally displaying the history of any collected data on any Light Point Controller | MR
| 7. Energy consumption: System energy consumption (daily, weekly, monthly, quarterly and annually over a user-defined time period) | MR
| D. The CMS shall be accessible to authorised individual users only by unique user identifier and password or other similarly secure approach. | MR
| E. The CMS shall be accessible to authorised third party applications through a secure API. | MR |  | [List available APIs]
| F. The CMS shall be capable of restricting user access to specific functions. These functions shall include the following: | MR
| 1. Creating and managing users and groups | SR
| 2. Installing/Commissioning/Removing/Replacing one or more Light Point Controllers | SR
| 3. Configuring one or more Light Point Controllers | SR
| 4. Applying a lighting strategy (switching and dimming times and levels based on photocell and/or astronomical clock and/or fixed times and/or events) | SR
| 5. Collecting, displaying and analysing luminaire and electrical failures on maps and reports | SR
| 6. Controlling and monitoring one or more Light Point Controlles in real time | SR
| 7. Report generation for failure, energy and other purposes | SR
| 8. Custom report generation | SR
| G. The CMS shall be accessible through a handheld mobile device (smart phone and/or tablet) in a format designed to accommodate the size and user interface of the mobile device. | SR
H. All asset data shall be stored on the CMS. It shall be capable of storing the following asset and warranty information for all Lighting Control Points:
| 1. Column number (Note: some lighting columns may be fitted with than one luminaire) | SR
| 2. Column type | SR
| 3. Light Point Controller unique identifier on the network | SR
| 4. Light Point Controller make, model and firmware version | SR
| 5. Column GPS location | SR
| 6. Column grouping | SR
| 7. Luminaire make and model | SR
| 8. Luminaire optic and/or light distribution description | SR
| 9. Luminaire nominal input voltage | SR
| 10. Luminaire system power (Luminaire and Light Point Controller) (Watts) | SR
| 11. Luminaire installation date | SR
| 12. LED power supply (driver) make and model and firmware version | SR
| 13. Electricity Retailer(s) and/or DNSP billing account number (there may be multiple retailers). | SR
| 14. Other information [Required information description] | SR
| I. The Central Management System shall be capable of Retrieving and Storing all remote monitoring data. | MR
J. Optional: The Central Management System shall integrate with the requirements of existing User systems (e.g. Council, Road Authority or DNSP):
| 1. Asset Management Systems (AMS) - [Specify particular systems] | SR
| 2. Works order and contract control systems - [Specify particular systems] | SR
| 3. User dashboards and citizen outage reporting systems - [Specify particular systems] | SR
4.3 Logical Features and Requirements
The Central Management System shall:
| A. Ensure secure communication between itself and all Light Point Controllers by enabling security features inherent to the underlying communications protocols; | MR
| B. Be capable of detecting communication failures between Light Point Controllers and the Central Management System and generate user alarms accordingly; | MR
| C. Be capable of updating Light Point Controller Firmware, auditing Light Point Controller Firmware version and identifying Light Point Controller Firmware corruption/hacking remotely and centrally, by group of Light Point Controllers; | MR
| D. Be capable of remotely monitoring Communication Network and Light point Controller performance, in order to identify and report any exception to normal operation; | MR
| E. Have open interfaces (API’s) for integration with other software from other vendors, e. g. Asset Management Systems; | MR
| F. Radio Frequency Communications Compliance: The system shall comply with all relevant regulations for Radio Frequency Communications as they apply to the particular system used in a country and/or region (eg AS/NZS CISPR 15); and | MR
| G. System Security: The system shall be manufactured, installed and commissioned so that appropriate levels of best practice system security are achieved. | SR
4.4 Functional Features and Requirements
The Central Management System shall be capable of:
| A. Commissioning new Light Point Controllers and sending configuration parameters to them (e.g. high/low voltage alarm threshold, luminaire nominal wattage) | SR
B. Collecting and storing the following online Lighting Control Point parameters:
| 1. Light Point Controller status (Online, Offline, Warnings, Errors) each time it changes | MR
| 2. Luminaire status (ON, OFF, Dimmed State, Warnings, Errors) each time it changes | MR
| 3. Input voltage (RMS) in ON state, with a new value every hour (24/7) as well as each time it changes by more than [X%] | SR
| 4. Input current (mA) in ON state, with a new value every hour (24/7) as well as each time it changes by more than [X%] | SR
| 5. Input active power (W) in ON state, with a new value every 30 mins (24/7) as well as each time it changes by more than [X%] | SR
| 6. Input power factor in ON state, with a new value every hour (24/7) as well as each time it changes by more than [X%] | SR
| 7. Cumulative ON state time (hours) | SR
| 8. Cumulative energy consumption (kWh) to align with AEMO (Australia) or EA (NZ) requirements | MR
| 9. GPS location (via integral sensor in Light Point Controller) | MR
Select any number of the following Options:
| 10. LED Power Supply (Driver) status (e.g. Warning or Error codes) if such data is made available by the power supply | SR
| 11. Ambient light level (via integral or external sensor) | SR
| 12. Ambient temperature (via integral or external sensor) if such data is made available by the power supply. | SR
| 13. Luminaire component(s) temperature (via integral sensor) | SR
| 14. Status of Pin 6 and Pin 7 of the Light Point Controller (in NEMA type Light Point Controller) | SR
C. Collecting events or failures detected by the Light Point Controller:
| 1. Luminaire; | SR
| 2. LED Power Supply (Driver) if such data is made available by the power supply; | SR
| 3. Mains voltage (either high or low voltage conditions, or total loss); | SR
| 4. Input current (either over or under current conditions, or total loss); | SR
| 5. Active input power (either over or under); | SR
| 6. Low power factor; | SR
| 7. High operating temperature; and | SR
| 8. Flickering LED module. | SR
| D. Programming the Reporting Frequency of online Lighting Control Point parameters for all Lighting Control Points. | MR
| E. Manual Control, whereby the On/Off and Dimmed state of a single Luminaire or group of Luminaires is modified via commands created by the Central Management System. | MR
F. Defining Luminaire groups to apply programs or calendars (e.g. via lasso tool on map)
| G. Creating Control Programs that are composed of a set of switch ON, switch OFF and stepless dimming commands (from 1% to 99%) | MR
| H. Creating Calendars that are composed of a set of Control Programs assigned to days of the year as requested by operator | MR
| I. Assigning Calendars, i.e. sets of control programs that use day and time, to groups of Luminaires and provide a mechanism to make sure these calendars are properly deployed in and executed by each Light Point Controller. | SR
J. Enabling Constant Light Output Control, whereby the Luminaire dimmed state is:
| Option 1: Actuated to achieve a desired light output in lumens. | SR
| Option 2: Automatically actuated to achieve a maintained Constant Light Output (lumens) over time by compensating for Luminaire lumen depreciation. | SR
K. The Central Management System shall be capable of creating reports (including trend graphing), pre-defined or customised, on-demand (displayed on screen) or scheduled (sent by email), for any group of Luminaires defined by a filter or by a geographical area, to analyse:
| 1. Assets, e.g. list the identifiers, address, number of operating hours and any other attributes selected by the User | SR
| 2. Alarms or failures, e.g. list the identifier, the GPS position, the Manufacturer and Model of Luminaire for any Light Point Controller that has an active Luminaire Failure and/or Communication Loss | SR
| 3. Energy Consumption, e.g. daily, weekly, monthly, quarterly or yearly energy consumption for any group of Luminaire | SR
| 4. Electrical network quality, e.g. list the identifier, the address and the Luminaire group and any other attributes selected by the User, for all the Luminaires where mains voltage was higher than [Voltage] at midnight last night | SR
L. The Central Management System shall be capable of generating configurable alarms and sending them to identified Users by email or text message (SMS) or by Application Programming Interface (API) in case of:
| 1. An event (e.g. Luminaire Failure event) is received by the CMS from a Light Point Controller | MR
| 2. A number of events (e.g. Communication Loss) are received from more than [Number] Light Point Controllers all located within a certain geographical area | SR
| 3. More than [Percentage] % of Light Point Controllers have failed within a group | SR
4.5 Interoperability - Central Management Systems
| A. Optional: The CMS shall be compliant with TALQ v 2.0 Specification | SR
B. The CMS shall be Interoperable with [Insert one or more of the following options]:
| 1. Analogue 0-10V compliant LED power supply; | SR
| 3. Digital DALI 2.0 compliant and certified LED power supply | SR
| 4. Zhaga Book 18 compliant Light Point Controllers | SR

## Schedule B (ii)
Returnable Schedule B (ii) Communication Networks
Tenderers should note that a non- compliant or partially compliant response to a Mandatory Requirement may result in the tender being rejected
|  | Recommendation about whether each item should be Mandatory Requirement (MR) or Scored Response (SR) | Short Response | Further Details | Links
5.1 Backhaul Specification [Select one or more, as desired]
A. Optional: The Backhaul Communication Network shall be provided by the User. It shall provide a minimum of secured encrypted IPv6 communication channels (if multiple port – list all ports required between the Field Device Communication Network (e.g. Gateways) and the Central Management System). It shall be [Select one or more, as desired]:
| 1. A fibre optic network that is operated by [Operator] and to which the Central Management System shall connect; | SR
| 2. A mobile phone network from [Operator] with whom the User has negotiated a global communication contract; and/or | SR
| 3. A WiFi network from [Operator]. | SR
| B. Optional: The System shall use a Backhaul Communication Network specified by the Vendor. | SR
C. Optional: The Vendor shall provide all available Backhaul Communication Network options:
| 1. EXCLUDING those which have pre-defined fees (e.g. Vendor negotiated mobile network contracts). | SR
| 2. INCLUDING those which have pre-defined fees (e.g. Vendor negotiated mobile network contracts). | SR
Field Device Communication Network Specification
6.1 Physical Features and Requirements
| A. Field Device Communication Network components shall be capable of normal operation over an ambient temperature range (according to EN 12368 Traffic control equipment - Signal heads) of [Select one or more, as desired]: | MR
| 1. -15 degrees C to +60 degrees C (hot environment) | MR
| 2. -25 degrees C to +55 degrees C (medium environment) | MR
| 3. -40 degrees C to +40 degrees C (cold environment) | MR
| B. Field Device Communication Network component enclosures installed external or remote to luminaires shall be rated to a minimum of IP65 (or a Vendor statement of suitability for the outdoor environment should be provided). | SR
| C. Field Device Communication Network components shall operate at 230V nominal (+10%/-6%) | MR
6.2 Logical Features and Requirements
The Communication Network shall:
| A. Use an open, standard-based physical layer for communication such as IEEE 802.15.4g for wireless mesh networks or Global System for Mobile communications (GSM) standards for mobile networks or LTE for Narrow Band IoT networks. | MR
| B. Be capable of connecting to Central Management Systems using open, standards based networking technologies such as http, SMTP, SNMP, COAP, TCP, UDP or FTP. | MR
| C. Ensure that all data communications over the Communication Network be secured using a standards based security protocol (e.g. TLS, DTLS, IPsec). | MR
| D. Allow only authenticated and authorised access to network services by a Central Management System, Gateway or Light Point Controller. | MR
| E. Be capable of maintaining accurate time either on its own or by synchronising with a remote service. | SR
| F. Provide a detailed view of the network and its topology, including all connected Gateways, Light Point Controllers, links, and ports. | SR
| G. Provide a real-time and historical detailed view of network performance, including available bandwidth, Gateways, Light Point Controller location, accessibility, signal strength, round-trip times, path costs, and packet delivery success/failure. | SR
| H. Provide a configuration management tool to view and remotely apply changes, updates, and patches to operating systems and applications on any single or a group of Field Device Communication Network components, including Gateways and Light Point Controllers. | SR
| I. Enable the operating system and applications to update all connected and active Gateways and Light Point Controllers within less than [Select an option]: | SR
| 1. 1 hour | SR
| 2. half day | SR
| 3. 1 day | SR
| J. Be capable of logging time-stamped activity. The logging level shall be configurable. Any write and execute operations completed by a Light Point Controller or Gateway shall be recorded together with the source IP address. | SR
| K. Provide basic firewall capabilities, including filtering by port, protocol, source IP address, and destination IP address. | SR
| L. Provide basic routing capabilities. The Gateway shall act as a multi-band Gateway, between the Backhaul Network and the Field Network. | SR
| M. Be capable of communicating using Internet Protocol version 6 (IPv6). Every device must be addressable via an assigned IPv6 address. | SR
| N. Radio Frequency Communications Compliance: Gateways, Light Point Controllers and the Network system shall comply with all relevant regulations for Radio Frequency Communications as they apply to the particular system used in a country and/or region (eg AS/NZS CISPR 15). | MR
| O. System Security: The system shall be manufactured, installed and commissioned so that appropriate levels of best practice system security are achieved. | SR
P. The Field Device Communication Network and any connected device or system shall [Select from the following options]:
| 1. Optional: Be able to authenticate each other by a standard-based mechanism (e.g. X.509 certificates or pre-shared keys). | SR
| 2. Optional Be able to authorise each other by a standard-based mechanism (e.g. X.509 certificates). | SR
| 3. Optional: Be kept confidential using a standard-based encryption algorithm (e.g. AES-128 or AES-256). | SR
| 4. Optional: Be checked for integrity using a standard-based algorithm (e.g. keyed HMAC with SHA-256). | SR
6.3 Functional Features and Requirements
The Communication Network shall be capable of:
| A. Two-way communication. | MR
| B. Automatically supporting failover to alternate routes. | SR
| C. Automatic retries while attempting to deliver messages/packets. | SR
| D. Generating asynchronous alerts and routing both Field Device Communication Network and other device alerts to the Central Management System. | SR
| E. Addressing of groups of Gateways and Light Point Controllers for bulk messages including remote firmware upgrades and configuration changes. | MR
| F. Allowing near real-time communication and: | SR
a. Receive and execute any manual override commands (ON/OFF/DIM) sent by the User from the Central Management System within less than [Select ONE Option]:
| 1. 5 seconds | SR
| 2. 30 seconds | SR
| 3. 1 minute | SR
b. Read and send any electrical parameter (or information) on any Light Point Controller within less than the following, when requested by the User through the Central Management System [Select ONE Option]:
| 1. 5 seconds | SR
| 2. 30 seconds | SR
| 3. 1 minute | SR
| G. Optional: Maintaining Network Availability for [Select ONE Option]: | MR
| 1. 95% | SR
| 2. 99.9% | SR
| of active and functional Gateways and Light Point Controllers at least [Select ONE Option]: | MR
| 1. 95% | SR
| 2. 98% | SR
| 3. 99% | SR
| of the time (other than for third party causes eg power cuts). The Vendor shall provide the tools to monitor the performance of such a Service Level Agreement. | SR
| 6.4 Interoperability | MR
| A. Optional: The Field Device Controller Communication Network shall be Interoperable with the following existing Light Point Controllers and Sensors [Insert description]. | SR
| 6.5 Rated Life and Reliability | MR
| A. The Rated Life of all Communication Network components at an ambient temperature of 25 degrees Celsius shall be greater than [Select ONE of the following options]: | MR
| 1. 10 years | SR
| 2. 15 years | SR
| 3. 20 years | SR
| B. The Vendor shall provide the predicted reliability of Field Device Communication Network components (Gateways and Routers) as measured calculated by Mean Time between Failures (MTBF) calculated according to Telcordia SR-332. | SR
| 6.6 Networked Standby Mode Power Disclosure | MR
| A. The Vendor shall disclose the Networked Standby Mode Power consumption (W) for Gateways and Routers. Networked Standby Mode Power is power consumption when connected to a supply voltage with all functions off, except for support functions using a trigger from a network. This is in accord with the forthcoming AS/NZS 63103. | MR

## Schedule B (iii)
Returnable Schedule B (iii) Light Point Controllers
Tenderers should note that a non- compliant or partially compliant response to a Mandatory Requirement may result in the tender being rejected
|  | Recommendation about whether each item should be Mandatory Requirement (MR) or Scored Response (SR) | Short Response | Further Details | Links
7.1 Light Point Controller Information
A.The Vendor shall supply the following Light Point Controller information:
| 1. Brand | MR
| 2. Type | MR
| 3. Model Number | MR
7.2 Physical Features and Requirements
A. Light Point Controllers shall be capable of operation over an ambient temperature range (according to EN 12368 Traffic control equipment - Signal heads) of [Select ONE of the following options]:
| -15 degrees C to +60 degrees C (hot environment) | MR
| -25 degrees C to +55 degrees C (medium environment) | MR
| -40 degrees C to +40 degrees C (cold environment) | MR
| B. Light Point Controller installed external or remote to luminaires shall be housed in enclosures rated to a minimum of IP65 | MR
| C. Light Point Controller shall operate at 230V (nominal (+10/-6%) | MR
D. Light Point Controllers shall be integrated (mechanically and electrically connected) at Lighting Control Points [Select ONE Option]:
| 1. External to Luminaires, using a NEMA/ANSI C136.41 7-pin receptacle for electrical and dimming control signal connectivity. | MR
| 2. External to Luminaires, using a Zhaga Book 18 40mm diameter Luminaire Extension Module for dimming control and sensor signal connectivity. | MR
| 3. External to Luminaires, using a Zhaga Book 18 80mm diameter Luminaire Extension Module for dimming control and sensor signal connectivity. | MR
| E. Optional: Field Device Light Point Controller integration compatibility shall be verified for all Luminaires specified in section 11 Appendix B: Existing Luminaires. | SR
| F. Light Point Controllers shall be capable of actuating the status (ON state, OFF state) of Luminaires. | MR
G. Light Point Controllers shall be capable of actuating a Luminaire Dimmed state by creating a control signal that [Select ONE or MORE options, as desired]:
| 1. Complies with analogue 0-10V standard (IEC 60929) | MR
| 2. Complies with, and is DiiA certified to, DALI 2.0 digital standard ( IEC 62386:2017) | MR
| 3. Complies with DALI 2.0 and is D4i certified as being compliant with Zhaga Book 18 Specification | MR
H. Actuated changes to Luminaire Dimmed states by Light Point Controllers shall occur at the following rate [Select ONE or MORE options, as desired]:
| 1. Instantaneously, or as dictated by the Luminaire | SR
| 2. Over a user programmable range (% change per minute) defined by the CMS | SR
| 3. Greater than [% change] per minute | SR
| 4. Less than [% change] per minute | SR
I. Light Point Controllers shall be capable of measuring and monitoring the following power parameters:
| 1. RMS input voltage (Volts) | MR
| 2. RMS input current (Amps) | MR
| 3. Active power (Watts) individually for Luminaire and LPC | MR
| 4. Power factor | MR
| 5. Optional: Frequency (Hz) | SR
| 6. Optional: Apparent power (VA) | SR
J. Light Point Controllers shall measure energy consumption (in kWh) of both Luminaire and the Light Point Controller itself to:
| 1. meet the requirements of the specific regional electricity regulator (if applicable). | SR
| 2. meet metering accuracy and precision of better than +/- 1.0% over a load range corresponding to the specific user-defined light level dimming or brightening range. | SR
K. Light Point Controllers shall incorporate internal surge protection (conforming to ANSI C136.2-2015) to [Select ONE or MORE, as desired]:
| 1 Not Required | SR
| 2 5 kV | SR
| 3 10kV | SR
| 4 20kV | SR
| 5 Other [Insert other] | SR
| L. Optional: Light Point Controller energy consumption accuracy shall be verified with all Luminaires specified in Appendix B; Existing luminaires. | MR
M. Light Point Controllers shall be capable of integrally sensing and monitoring over time the following environmental parameters [Select ONE or MORE, as desired]:
| 1. Expected sunrise and sunset times (e.g. via an Astronomical Clock or via the CMS) | SR
| 2. Ambient light level | SR
| 3. GPS Location | SR
| 4. Ambient temperature | SR
| 5. Other (specify) | SR
| N. Light Point Controllers shall be capable of logging energy consumption in minimum of 30 minute increments or be otherwise capable of accurately deriving energy consumption based on recording of a change in electricity consumption (unless another interval or requirement is otherwise required by the relevant electricity regulator) and also Cumulative energy consumption of each Light Control Point. | SR
O. Light Point Controller shall log cumulative energy consumption according to the following specifications [Select ONE or MORE, as desired]:
| 1. IEC 61968-9 Meter Reading and Control | MR
| 2. The requirements specified by [Name of the relevant electricity regulator, electricity DNSP and/or electricity retailer], as documented in [Electricity DNSP and/or electricity retailer] references to appropriate standards or specifications as applicable – Include relevant excerpts in Appendix if appropriate] | MR
P. Optional: During Offline Operation (i.e. when the network is down), Light Point Controller shall be capable of Storing the following offline Time-Stamped Control Point parameters:
| 1. Controller status (Online, Offline, Warning or Error codes) | SR
| 2. Luminaire status (ON, OFF, Dimmed State, Warning or Error codes) | SR
| 3. Cumulative ON state time (minutes) | SR
| 4. Cumulative energy consumption (kWh) | SR
Q. Optional: During Offline Operation Light Point Controller shall be capable of storing measurements of identified Offline Parameters at a storing frequency of less than once every [Select ONE Option]:
| 1. 1 Hour | SR
| 2. 2 Hours | SR
| 3. 6 Hours | SR
| 4. 12 Hours | SR
as well as when these values change by more than [Select an option]:
| 1. 5% | SR
| 2. 10% | SR
| 3. 15% | SR
so that all important values are recorded and later sent to the Central Management System.
R. Optional: During Offline Operation Light Point Controller shall be capable of storing measurements of all Offline Parameters at the specified frequency for a Storing Period of greater than [Select ONE Option]:
| 1. 2 Days | SR
| 2. 3 Days | SR
| 3. 7 days | SR
| 4. As required by the electricity market regulator | SR
S. Optional: If a Light Point Controller loses electrical service due to an unforeseen event, the Light Point Controller shall:
| 1. Be capable of communicating the loss of electrical service to the Central Management System and/or to Light Point Controller in the neighbourhood, which will send it to the Central Management System. | MR
| 2. Be capable of communicating any Light Point Controller stored data to the Central Management System | MR
| T. Be capable of self-commissioning without user input | SR
7.3 Logical Features and Requirements
A. During Online Operation, Light Point Controller shall be capable of Reporting the following online Control Point parameters:
| 1. Light Point Controller status (Online time, Offline time, Warning or Error codes) | SR
| 2. Luminaire status (ON, OFF, Dimmed State, Warning or Error codes) if the Power Supply can provide such information | SR
| 3. Average RMS input voltage (Volts) in the ON state | SR
| 4. Average RMS input current (Amps) in the ON state | SR
| 5. Average true input power (Watts) in the ON state | SR
| 6. Average active power factor in the ON state | SR
| 7. Cumulative ON state time (minutes) | SR
| 8. Cumulative energy consumption (kWh) | SR
| 9. GPS location (via integral sensor) | SR
| 10. Optional: LED Power Supply status (e.g. Warning or Error codes) if the Power Supply can provide such information. | SR
| 11. Optional: Ambient Temperature (via integral sensor) | SR
| 12. Optional: LED Power Supply operating temperature | SR
B. During Online Operation, Light Point Controllers shall be capable of reporting all online Control Point parameters for all Light Control Points when these values change by more than [Select ONE Option]:
| 1 5% | SR
| 2 10% | SR
| 3 15% | SR
| C. and at a minimum Reporting Frequency of once per day [or other interval as specified] | SR
D. During Online Operation, Light Point Controller shall be capable of answering any request for real-time reading of all Light Point Controller parameters for a single Light Point Controller at a maximum of [Select ONE option]:
| 1. 5 seconds | SR
| 2. 10 seconds | SR
| 3. 30 seconds | SR
| 4. 1 minute | SR
| 5. 5 minutes | SR
E. Light Point Controllers shall execute any single command received from the Field Device Communication Network in less than [Select ONE option]:
| 1. 1 second | SR
| 2. 5 seconds | SR
| 3. 15 seconds | SR
| 4. 30 seconds | SR
| 5. 60 seconds | SR
| F. Light Point Controller shall automatically Report all data Stored during Offline Operation, when Online Operation is restored. | MR
| G. Light Point Controller shall include a method to verify the integrity of firmware to be executed, to prevent unauthorised or maliciously modified software from running on the Light Point Controller. This could, for example, use a secure Boot Loader scheme. | SR
| H. Radio Frequency Communications Compliance: The system shall comply with all relevant regulations for Radio Frequency Communications as they apply to the particular system used in a country and/or region. | MR
| I. System Security: The system shall be manufactured, installed and commissioned so that appropriate levels of best practice system security are achieved. | MR
7.4 Logical Features and Requirements
Light Point Controller shall be capable of:
| A. Controlling a single Luminaire or groups of Luminaires. | MR
| B. Optional: Changes in the On/Off or Dimmed states to groups of Luminaires shall be staggered to limit the inrush current through other electrical components on the electrical circuit. | SR
| C. Manual Control, whereby the On/Off and Dimmed state of a single Luminaire or group of Luminaires is modified in response to commands from the Central Management System. | MR
| D. Manual Control, whereby the On/Off and Dimmed state of a single Luminaire or group of Luminaires is modified in response to commands from another LPC that has a directly attached Sensor. | SR
| E. Group Control, whereby Luminaire groups are controlled by programs or calendars (e.g. via lasso tool on map). | MR
F. Control Programs, that are composed of a set of switch ON, switch OFF and stepless dimming commands (from 1% to 99%) defined at:
| 1. Any fixed time (hours, minutes) with at least [Appropriate number] of such events per day; | SR
| 2. Or any sun-related time (e.g. sunrise plus 7 minutes, sunset minus 5 minutes); | SR
| 3. Or any photocell-related event (applicable if the Light Point Controller has photocell); | SR
| 4. Or any other events received from sensors (e.g. presence or activity sensor) to dynamically adjust light levels based on activity; | SR
| 5. Or any input from Traffic Counting Devices to dynamically adjust light levels based on traffic density. | SR
G. Calendar Control, from a set of Control Programs assigned to days of the year:
| 1. On a daily recurring basis; | MR
| 2. Or on a weekday recurring basis; | MR
| 3. Or on a weekend recurring basis; | MR
| 4. Or on a special date/time period for special events. | MR
| H. Assigned Calendar Control, i.e. sets of Control Programs, to groups of Luminaires providing a mechanism to ensure Calendars are properly deployed and executed by each Light Point Controller. | MR
| I. Control Programs that provide Luminaire signaling to provide alerts to the community (e.g. luminaire flashing. | SR
J. During Offline Operation Light Point Controller shall be capable of maintaining Luminaire control by:
| 1. Storing the Control Program in the Light Point Controller to run even if the network is not present; | MR
| 2. Continuing to operate according to the most recently programmed Scheduled Control; and | SR
| 3. Continuing to operate according to the most recently programmed Adaptive Control using input from an integral sensor. | SR
| K. Optional: True input power control, whereby the Luminaire Dimmed state is actuated to achieve to a desired true input power (Watts). | SR
| L. Optional: Light output control, whereby the Luminaire Dimmed state is actuated to achieve a desired light output (lumens). | SR
| M. Optional: Automatically maintaining constant Luminaire light output (lumens) over time by compensating for Luminaire lumen depreciation. | SR
7.5 Interoperability
The system shall provide interoperability at various levels:
A. Optional: Between Central Management System and Field Device Communication Network:
| 1. The Central Management System shall be certified as compliant with the TALQ Central Management System (CMS) specification v____ | MR
| 2. The Field Device Communication Network shall be certified with TALQ Outdoor Lighting Network (OLN) specification v____ | MR
B. Optional: Between Field Device Communication Network and Light Point Controller. The Field Device Communication Network shall accept, communicate with and interact with the following number of Light Point Controller from independent Vendors [Select ONE option]:
| 1. 3 | SR
| 2. 4 | SR
| 3. 5 | SR
| 4. 6 | SR
List of Vendors HERE:
C. Between Light Point Controller and Luminaire:
| 1. Optional: Interoperable with analogue 0-10 V compliant LED Power Supplies | MR
| 2. Optional: Interoperable with digital DALI 2.0 certified LED Power Supplies | MR
| 3. Optional: Interoperable with Zhaga Book 18 certified interface and LED Power Supplies | MR
| 4. Optional: Interoperable with the Luminaires specified in Appendix B: Existing Luminaires | SR
| D. Optional: The Vendor shall agree to demonstrate Light Point Controller Interoperability with the existing Luminaires described in Appendix B: Existing Luminaires, prior to Installation. | SR
7.6 Rated Life & Reliability
A. The Rated Life of all Light Point Controllers at an ambient temperature of 25 degrees Celsius shall be [Select ONE option]:
| 1. 10 years or more | MR
| 2. 15 years or more | MR
| 3. 20 years or more | MR
| B. The Vendor shall report the predicted reliability of the following Light Point Controllers, as calculated by Mean Time between Failures (MTBF) according to Telcordia SR-332s. | MR
7.7 Networked Standby Mode Power Disclosure
| A. The Vendor shall disclose the Networked Standby Mode Power consumption (W) for Light Point Controllers. Networked Standby Mode Power is power consumption when connected to a supply voltage with all functions off, except for support functions using a trigger from a network. This is in accord with the forthcoming AS/NZS 63103. | MR

## Schedule B (iv)
Returnable Schedule B (iv) Installation & Maintenance
Tenderers should note that a non- compliant or partially compliant response to a Mandatory Requirement may result in the tender being rejected
|  | Recommendation about whether each item should be Mandatory Requirement (MR) or Scored Response (SR) | Short Response | Further Details | Links
8.2 System Installation Responsibility
A. Installation shall be performed by the responsible party [Select ONE option]:
| 1. The Vendor or its nominated sub-contractor | MR
| 2. The following third party: [Third party name] | MR
| B. All hardware necessary for installation and provisioning for network communication shall be provided by the Vendor. | MR
8.3 System Installation Training Requirements
| A. If the Vendor is not the responsible party, the Vendor shall provide training on the installation of Gateways and other components (if applicable) to the responsible party and provide a reasonable estimate in Schedule C of the typical component installation time. | MR
| B. The responsible party shall provide installation training manuals and all supporting documentation in electronic format. | MR
8.4 System Installation Requirements
The responsible party shall:
| A. Specify whatever coordination is needed with the User's IT staff. | MR
| B. Mount and electrically connect all Gateways, Light Point Controllers (if applicable) and other Components (as applicable) in a location sufficiently removed from sources of electromagnetic radiation that are likely to interfere with System Performance. The Vendor shall specify minimum acceptable distances. | MR
| C. Inspect the installed System following the installation of all Components and verify that the System is capable of operating as intended. | MR
| D. Ensure that a licensed electrician from the responsible party shall inspect the installed System after it has been fully energized and submit the regionally appropriate electrical installation Certificate of Compliance (CoC) and/or SDoC as per the requirements of AS/NZS 3000 and applicable local requirements, and/or EMC Compliance Declaration. | MR
| E. Submit a brief written report of any defective materials and workmanship issues found during inspections, as well as any unsatisfactory test results. | MR
| F. Submit a brief written report containing a list of all installed components, tests performed, test results, as-built drawings and with a final signoff by the responsible party. | MR
8.6 System Start-Up Responsibility
A. System Start-up (pre-commissioning) shall be performed by [Select ONE Option]:
| 1. The Vendor or its nominated sub-contractor | MR
| 2. The following third party: [Third party name] | MR
| B. All hardware, software and tools necessary for System Start-up shall be provided by the Vendor. | MR
8.7 System Start-Up Training Requirements
| A. The responsible party shall provide System Start-up training manuals and all supporting documentation. | MR
8.8 System Start-Up Requirements
The responsible party shall:
| A. Identify a manufacturer-authorised representative available to support System Start-up. | MR
| B. Specify coordination needed with the User's IT staff in order to complete System Start-up. | MR
| C. Configure any hardware, firmware, or software to enable all System Components to operate as intended. | MR
| D. Ensure that the latest versions of all firmware and software are installed, and perform any necessary updates or upgrades. | MR
| E. Successfully demonstrate all System functions and capabilities System Start-up training. | MR
| F. Ensure that following User acceptance of a successful demonstration of all System functions a System Start-up trial period shall commence. | MR
G. Ensure that the System Start-up proving period shall consist of [Select ONE option]:
| 1. 3 consecutive calendar days of System operation | MR
| 2. 7 consecutive calendar days of System operation | MR
| H. Ensure that all System functions shall operate normally for at least ninety-nine percent (99%) of the time. | MR
| I. Remedy any issues discovered during the System Start-up trial period. | MR
| J. Provide written documentation of all hardware, firmware, or software configurations and all modifications made in System Start-up, and shall accurately represent the System following a successful System Start-up proving period. | MR
8.10 System Commissioning Responsibility
A. System Commissioning training shall be performed by [Select ONE Option]:
| 1. The Vendor | MR
| 2. The Vendor-specified agent or representative | MR
B. System Commissioning shall be performed by [Select ONE Option]:
| 1. The Vendor | MR
| 2. The Vendor-specified agent or representative | MR
| 3. The following Third Party: [Third Party Name] | MR
8.11 System Commissioning Training Requirements
| A. The responsible party shall provide Commissioning training manuals and all supporting documentation in electronic Format | MR
8.12 System Commissioning Requirements
The responsible party shall:
| A. Identify a manufacturer-authorised representative that will be available to support System Commissioning. | MR
| B. Modify any System software settings as necessary to configure all System functions. | MR
| C. Optional: [When DALI 2.0 has been selected, include the following] Ensure and successfully demonstrate that the CMS accommodates standardised data field allocations for asset management parameters and successfully uploads these as per DiiA Specification for DALI-2 Part 251 Memory Bank 1 Extension. | MR
| D. Successfully demonstrate all that System functions are performing according to User desires. | MR
| E. Ensure that following User acceptance of a successful demonstration of all System functions performing according to User desires, a System Commissioning trial period shall commence. | MR
F. Ensure that the System Commissioning period shall consist of [Select ONE option]:
| 1. 7 consecutive calendar days of System operation | MR
| 2. 14 consecutive calendar days of System operation | MR
| G. Ensure that all System functions shall operate according to User Specification for at least ninety-nine percent (99%) of the time (after commissioning). | MR
| H. Remedy issues discovered during the System Commissioning trial period. | MR
| I. Submit written documentation of all System software settings required to configure all System functions according to User desires. Written documentation of all System software settings shall include all modifications made over the course of System Commissioning, and shall accurately represent the System following the completion of a successful System Commissioning trial period. | MR
| J. Allow the User to undertake (at User cost) a post-commissioning lighting and control system site measurement and verification process of the complete lighting system (control system and installed luminaires) to confirm that the Vendor has delivered the lighting outcomes intended (as applicable to controls). This may be undertaken using the provisions of European Standard EN 13201-4:2015 Road Lighting Part 4: Methods of measuring lighting performance and Annexe D - Guidelines for measurement systems for adaptive road lighting. Other methods, including vehicular based dynamic lighting measurement techniques may be used for measurement and verification or check testing of lighting control system outcomes. | MR
9.1 Maintenace Responsibility
A. The System shall be maintained by [Select ONE Option]:
| 1. The Vendor | MR
| 2. The Following Third Party: [Third party name] | MR
| 3. The User | MR
| B. In the case that the Vendor is maintaining the System, the Vendor shall provide an overall description of its maintenance plan and its reactive and proactive service capabilities to meet that plan (if applicable). | SR
9.2 Maintenace Requirements
A. If the System is maintained by a Third Party or the User:
| 1. The Vendor shall provide comprehensive maintenance training at User premises, covering all aspects of the System; | MR
| 2. The Vendor shall provide hardware and software maintenance and support according to the warranty terms for the duration of the warranty period. Any Maintenance term shall start following the end of the applicable warranty period; | MR
| 3. The Vendor shall specify any mandatory maintenance required to maintain the terms of the warranty; and | MR
| 4. Optional: Software and firmware upgrades, maintenance and support shall be provided for one year at no additional cost. The Vendor shall notify the User of any planned firmware updates, obtain User approval prior to making all changes and provide a process for reversing any changes if any faults or unwanted issues are identified. | SR
| 5. Optional: The Vendor shall provide onsite assistance if remote support cannot resolve maintenance issues. | SR
B. If the System is maintained by the Vendor:
| 1. The responsible party shall be responsible for the complete maintenance of the System, ensuring compliance with all terms of the Specification at all times; | MR
| 2. If the Vendor is hosting the system, Vendor shall provide a comprehensive backup plan for software/system/server services, and stored data; | MR
| 3. Optional: Monthly maintenance records and reports shall be submitted to the User. These shall include inspection reports, documentation of maintenance performed, and expected future maintenance requirements; and | SR
| 4. Optional: The Vendor shall provide a mechanism to allow the User to submit requests for addressing any System malfunctions or maintenance issues. | SR
| C. Measurement and verification for routine maintenance and warranty enforcement: Any time after installation and commissioning the User may undertake (at User cost) lighting and control system site measurement and verification process of the complete lighting system (control system and installed luminaires) to confirm adequate maintenance of the lighting outcomes intended (as applicable to controls). This process may be undertaken using the provisions of European Standard EN 13201-4:2015 Road Lighting Part 4: Methods of measuring lighting performance. Annexe D - Guidelines for measurement systems for adaptive road lighting. Other methods, including vehicular based dynamic lighting measurement techniques may also be used for measurement and verification or check testing of lighting and control system outcomes. | MR
D. The Vendor shall:
| 1. Hold appropriate quantities of spares that it is able to despatch within 24 hours of notification. | MR
| 2. Provide a 24 hour facility to receive and address requests for technical support. | MR

## Schedule C
Returnable Schedule C - Pricing
Tenderers should note that two proposal options are avaialble for pricing of the Communication Network. All capital and on-going components must be priced. If no cost is applicable enter N/A
| Pricing Component | Initial Cost ($ per unit or lump sum as indicated excl GST) | On-Going Annual Cost ($ per unit or lump sum as indicated excl GST) | Time | Quantity Required | Comments (including delivery lead time in weeks if applicable)
1 | Software Costs
1.1 | CMS software (licence, hosting, maintenance and updates) | $/unit or lump sum | $/unit or lump sum | NA |  | [Include duration of offer, in years]
1.2 | Other software licences required (eg firmware licences, maintenance and updates) | $/unit or lump sum | $/unit or lump sum | NA |  | [Include duration of offer, in years]
2A | Communication Network Costs - Option 1: Customer-owned and maintained
2A.1 | Hardware (eg Gateways) | $/unit | NA | NA
2A.2 | Annual costs (including annual connection, backhaul, connection-as-a-service or any other on-going costs) | NA | $/unit | NA |  | [Include duration of offer, in years]
2A.3 | Installation training | $ (lump sum) | NA | NA
2A.4 | Installation tools required | $ (lump sum) | NA | NA
2A.5 | Estimated time and resources for customer to install per gateway | NA | NA | hr/unit |  | [Clearly state installation assumptions]
2A.6 | Estimated time and resources for customer to maintain system | NA | NA | hr/yr |  | [Clearly state installation assumptions]
2B | Communication Network Costs - Option 2 - Tenderer-owned, installed & operated
2B.1 | Initial and on-going network-as-a-service costs (including all initial capital costs and on-going connection (including backhaul) and maintenance costs) | $/unit or lump sum | $/unit | NA |  | [Include duration of offer, in years]
3 | Light Point Controller Costs
3.1 | LPC unit capital cost | $/unit | NA | NA
3.3 | Installation / commissioning tools required | $ (lump sum) | NA | NA
4 | Training and Support Costs
4.1 | Tenderer-provided system training for customer on commissioning | $ (lump sum) | NA | NA
4.2 | Estimated cost, time and resources for Tenderer to provide customer system integration support | $ (lump sum) | $/hr for additional support | Estimated hours for initial system integration
4.3 | Ongoing support | NA | $/hr for additional support if not included in on-going fees | NA |  | [Include duration of offer, in years]
5 | Other Costs
5.1 | Any other capital or on-going costs not covered in the above (including project management fees, API costs, API integration costs etc.) | $/unit or lump sum | $/unit or lump sum | NA |  | [Add additional lines as needed to seperately delineate different additional costs. Include duration of each offer, in years, if applicable]